## Slide 1
TITLE PAGE
Problem Statement ID - 1
Problem Statement Title- Eco-Loop Building Agents: AI-Powered Autonomous Smart Building Optimization Challenge
Theme- Clean & Green Technology (Smart Automation / Sustainable Energy)
PS Category- Software
Student Name (Registered on portal)- Mahendra Kausik Vankadara
Student ID- PES1UG23AM163

## Slide 2: Eco-Loop: A Self-Correcting Building That Negotiates Its Own Energy Use
Proposed Solution:
What it is:
  A closed control loop: EnergyPlus simulates a real 5-zone building; an open-weight LLM (gpt-oss-120b) reads live zone state every simulated hour and injects new HVAC setpoints back into the running simulation- one process, in-memory, no human in the loop.
  The LLM doesn't just react to temperature. It reasons against a 24 h grid carbon-intensity + tariff forecast, occupancy lookahead, weather lookahead, CO₂/IAQ, humidity, and a peak-demand threshold then pre-cools into clean, cheap hours and sets back hard when the building empties.
How it addresses the problem:
  Traditional BMS runs rigid schedules. Measured on a matched 7-simulated-day run, same weather, same building: −8.8% total facility electricity, -23.3% HVAC-only electricity, and comfort improved 12.4 points (80.7% -> 93.1% of occupied hours with PMV in [-0.5, +0.5]).
  Savings are not taken out of occupants' comfort- the usual trade-off is inverted. Reheat gas also fell 32.9 -> 3.6 kWh and peak demand 19.9 -> 19.0 kW.
Innovation / uniqueness:
  A safety supervisor wraps the LLM: schema validation -> hard clamps -> anti-thrash rate limiter -> watchdog timeout -> deterministic rule-based fallback. The simulation cannot be killed by a bad, slow, or absent LLM response. A full run completes with the LLM entirely unreachable (shipped as proof).
  The LLM beats its own deterministic fallback on energy, HVAC energy, AND comfort simultaneously so the intelligence is doing measurable work, not just adding risk.
  Genuine self-correction: the agent was wasting 20+ kWh/day coasting into an empty building because the state digest described the previous hour. Adding one explicit decision_hour_occupied signal let the model fix itself- no supervisor override needed.

## Slide 3: TECHNICAL APPROACH
Technologies Used:
Python 3.11; EnergyPlus 26.1 driven through its bundled pyenergyplus runtime API with in-process callbacks (not file-rewrite-and-rerun, not FMU/BCVTB)
gpt-oss-120b (OpenAI open-weight), served OpenAI-compatible on Cerebras+Groq, round robined per call; local Ollama documented as a fully offline option
FastMCP: MCP server exposing the same 5 tools; Pydantic for strict-JSON decision validation; Plotly for the self-contained offline dashboard; pandas/numpy for metrics
Building model: shipped 5ZoneAirCooled.idf, Chicago TMY3 weather, 15-21 July
Methodology:

## Slide 4: FEASIBILITY AND VIABILITY
Feasibility (Measured, not projected):
  Runs today on free-tier infrastructure. 168/168 hourly decisions injected, 0 controller errors, 165/168 genuine LLM calls, latency p50 816ms / p95 2120ms against a 15s watchdog ~7x headroom.
  Reliability soak: 14 simulated days (2× the required horizon) with the LLM live throughout- 336/336 decisions injected, 0/336 fell back to the rule schedule, 0 crashes, latency p50 693ms / p95 1641ms, and 92.9% occupied comfort held across the full 14 days.
  Energy figures come from EnergyPlus's own meter file (eplusmtr.csv), not self-reported totals, so the headline can't be doubted.
Challenges and risks:
  ~62% of facility electricity is lighting/plug load no setpoint can touch which caps the achievable total-kWh%
  Free-tier LLM rate limits: an early run had only 43% genuine LLM participation
  LLM could return invalid, slow, or no output mid-run
  Naive energy accounting silently over-counted by 16.5%
Strategies that resolved each:
  Report HVAC-only % as the honest headline alongside total- state the ceiling rather than hide it
  Measured the actual binding limit per provider (they invert: Groq token-bound, Cerebras request-bound) -> per-provider throttles + round-robin took participation 43% -> 98%.
  The safety supervisor: clamp + watchdog + deterministic fallback. A 100%-fallback run is shipped as proof the loop survives a total LLM outage
  Caught it by reconciling against E+'s own meters; the smoke test now asserts agreement within 0.5% as a permanent regression guard (reconciles to 0.00%)
  Method, not luck: Two optimizations (CO₂-gated fan-off, optimal-start pre-heat) were built, measured, and reverted when the data showed no net benefit- negative results documented, not buried.

## Slide 5: ARTIFACTS
Full source: https://github.com/mahendra-kausik/eco-loop-building-agents
Architecture doc: docs/ARCHITECTURE.md: tool-calling, prompt strategy, latency management, long-log handling
Dashboard: results/dashboard.html
Building models: models/baseline.idf + agent_llm_runtime.idf / agent_fallback_runtime.idf (the actual applied hour-by-hour schedules baked into real IDF objects, diffable against baseline)
Decision log: results/decision_log.jsonl (168 decisions with the model's own stated reasoning) + decision_log_llm_unreachable.jsonl (the 100%-fallback proof run)
Reliability soak log: results/decision_log_soak14.jsonl (336 decisions, 14 simulated days, 0 fallbacks) plus the soak strip on results/dashboard.html
Metric | Baseline | AI closed loop | Result
Total electricity | 1100.1 kWh | 1003.6 kWh | −8.8%
HVAC-only electricity | 413.7 kWh | 317.3 kWh | −23.3%
Comfort (PMV in band, occupied) | 80.7% | 93.1% | +12.4 pts
Reheat gas | 32.9 kWh | 3.6 kWh | −89%
Peak demand | 19.9 kW | 19.0 kW | −0.9 kW
CO₂ (grid-weighted) | 663.8 kg | 602.2 kg | −61.6 kg
Cost @ ₹6/kWh | ₹6079 | ₹5485 | −₹594
Crash-free horizon | - | 14 sim days | 336/336, 0 fallback

## Slide 6: RESEARCH AND REFERENCES
EnergyPlus documentation & Python Plugin/API guide: energyplus.net (US DOE)
ASHRAE Standard 55 / Fanger PMV thermal comfort model: the basis of the [−0.5, +0.5] comfort band
Model Context Protocol (MCP) specification: modelcontextprotocol.io
gpt-oss-120b (OpenAI open-weight model), served via Cerebras and Groq OpenAI-compatible APIs
ASHRAE Standard 62.1: ventilation / CO₂ generation defaults used for the IAQ tracer